## coal
State | Facility Name | Facility ID (ORISPL) | Unit ID | Year | Operating Time | Notes | Nameplate Capacity (MW) | Nameplate Capacity Factor | Heat Rate (mmbtu/kwhr) | Case 1 MW-h (85% or Higher) | Nox ER | SO2 ER | NOx (tons) | SO2 Tons | Gross Load (MW-h) | Avg. NOx Rate (lb/MMBtu) | SO2 ER | NOx (tons) | SO2 (tons) | CO2 (short tons) | Heat Input (MMBtu) | Owner | Operator | Unit Type | Fuel Type (Primary) | Fuel Type (Secondary) | SO2 Control(s) | NOx Control(s)
ND | Antelope Valley | 6469 | B1 | 2014 | 7029.78 | LNB + SOFA installed | 434.9 | 77.19% | 10582.1635 | [5 empty] | 2940648.32 | 0.2013 | 0.37332 | 3195.961 | 5808.578 | 3387856.164 | 31118421.254 | Basin Electric Power Cooperative | Basin Electric Power Cooperative | Tangentially-fired | Coal |  | Dry Lime FGD | Overfire Air (Retired May 27, 2014)<br>Low NOx Burner Technology w/ Closed-coupled/Separated OFA (Began May 28, 2014)
ND | Antelope Valley | 6469 | B1 | 2015 | 8290.67 |  |  | 92.13% | 10574.237 | [5 empty] | 3509998.09 | 0.1121 | 0.34011 | 2103.443 | 6311.667 | 4040770.657 | 37115551.676 | Basin Electric Power Cooperative | Basin Electric Power Cooperative | Tangentially-fired | Coal |  | Dry Lime FGD | Low NOx Burner Technology w/ Closed-coupled/Separated OFA
ND | Antelope Valley | 6469 | B1 | 2016 | 8374.06 |  |  | 94.26% | 10344.3711 | [5 empty] | 3591136 | 0.1257 | 0.39057 | 2357.843 | 7254.497 | 4044308.351 | 37148043.568 | Basin Electric Power Cooperative | Basin Electric Power Cooperative | Tangentially-fired | Coal |  | Dry Lime FGD | Low NOx Burner Technology w/ Closed-coupled/Separated OFA
ND | Antelope Valley | 6469 | B1 | 2017 | 7328.78 |  |  | 80.86% | 9839.9118 | 94% | 2017 | 2017 |  |  | 3080412.14 | 0.1089 | 0.347 | 1661.912 | 5258.977 | 3299952.954 | 30310983.816 | Basin Electric Power Cooperative | Basin Electric Power Cooperative | Tangentially-fired | Coal |  | Dry Lime FGD | Low NOx Burner Technology w/ Closed-coupled/Separated OFA
[8 empty] | Average HR = | 10335.1709 | 3581140.56 | 0.1089 | 0.347 | 2015.287 | 6421.5559
ND | Antelope Valley | 6469 | B2 | 2014 | 8133.89 |  | 434.9 | 86.46% | 11060.1403 | [5 empty] | 3293979.29 | 0.3223 | 0.38291 | 6052.457 | 6975.007 | 3966339.668 | 36431873.049 | Basin Electric Power Cooperative | Basin Electric Power Cooperative | Tangentially-fired | Coal |  | Dry Lime FGD | Overfire Air
ND | Antelope Valley | 6469 | B2 | 2015 | 8582.32 |  |  | 94.49% | 10991.1576 | [5 empty] | 3599799.91 | 0.3601 | 0.33951 | 7283.115 | 6716.424 | 4307548.36 | 39565968.176 | Basin Electric Power Cooperative | Basin Electric Power Cooperative | Tangentially-fired | Coal |  | Dry Lime FGD | Overfire Air
ND | Antelope Valley | 6469 | B2 | 2016 | 6618.65 | LNB + SOFA installed |  | 72.25% | 10688.0121 | [5 empty] | 2752700.5 | 0.1832 | 0.34593 | 2683.185 | 5088.794 | 3203056.571 | 29420896.161 | Basin Electric Power Cooperative | Basin Electric Power Cooperative | Tangentially-fired | Coal |  | Dry Lime FGD | Overfire Air (Retired Jun 10, 2016)<br>Low NOx Burner Technology w/ Closed-coupled/Separated OFA (Began Jun 11, 2016)
ND | Antelope Valley | 6469 | B2 | 2017 | 8506.57 |  |  | 94.48% | 10432.0534 | 94% | 2017 | 2017 |  |  | 3599545.79 | 0.1081 | 0.40494 | 2044.9 | 7602.908 | 4088141.815 | 37550653.725 | Basin Electric Power Cooperative | Basin Electric Power Cooperative | Tangentially-fired | Coal |  | Dry Lime FGD | Low NOx Burner Technology w/ Closed-coupled/Separated OFA
[8 empty] | Average HR = | 10792.8408 | 3581140.56 | 0.1081 | 0.40494 | 2089.0693 | 7825.6311
SD | Big Stone | 6098 | 1 | 2014 | 8325.25 |  | 450 | 71.67% | 10633.7847 | [5 empty] | 2825223.46 | 0.687 | 0.92167 | 10506.842 | 13844.714 | 3150887.17 | 30042817.996 | Montana Dakota Utilities Company, Northwestern Public Service Company, Otter Tail Power Company | Otter Tail Power Company | Cyclone boiler | Coal | Diesel Oil, Wood |  | Overfire Air
SD | Big Stone | 6098 | 1 | 2015 | 4628.01 | outage for installation of new controls |  | 39.66% | 10636.3904 | [5 empty] | 1563250.85 | 0.3378 | 0.57792 | 3147.629 | 4804.668 | 1743875.99 | 16627346.262 | Montana Dakota Utilities Company, Northwestern Public Service Company, Otter Tail Power Company | Otter Tail Power Company | Cyclone boiler | Coal | Diesel Oil, Wood | Dry Lime FGD (Began Aug 31, 2015) | Overfire Air<br>Selective Catalytic Reduction (Began Aug 26, 2015)
SD | Big Stone | 6098 | 1 | 2016 | 7844.97 | first full year of new controls |  | 55.52% | 10749.1276 | [5 empty] | 2188752.57 | 0.0825 | 0.070303 | 961.881 | 827.015 | 2467530.794 | 23527180.736 | Montana Dakota Utilities Company, Northwestern Public Service Company, Otter Tail Power Company | Otter Tail Power Company | Cyclone boiler | Coal | Diesel Oil, Wood | Dry Lime FGD | Overfire Air<br>Selective Catalytic Reduction
SD | Big Stone | 6098 | 1 | 2017 | 7817.95 |  |  | 55.35% | 10867.4931 | 85% | 2017 | 2017 |  |  | 2182037.43 | 0.0846 | 0.071323 | 984.486 | 845.655 | 2487044.484 | 23713276.71 | Montana Dakota Utilities Company, Northwestern Public Service Company, Otter Tail Power Company | Otter Tail Power Company | Cyclone boiler | Coal | Diesel Oil, Wood | Dry Lime FGD | Overfire Air<br>Selective Catalytic Reduction
[8 empty] | Average HR = | 10721.6989 | 3350700 | 0.0846 | 0.071323 | 1519.6358 | 1281.1524
ND | Coal Creek | 6030 | 1 | 2014 | 7985.05 |  | 604.8 | 89.18% | 9796.3334 | [5 empty] | 4724860.89 | 0.2026 | 0.34069 | 4696.818 | 7884.754 | 5039198.139 | 46286312.341 | Great River Energy | Great River Energy | Tangentially-fired | Coal |  | Wet Lime FGD | Low NOx Burner Technology w/ Closed-coupled/Separated OFA
ND | Coal Creek | 6030 | 1 | 2015 | 8404.34 |  |  | 90.16% | 9851.5556 | [5 empty] | 4776889.23 | 0.2188 | 0.32585 | 5087.042 | 7667.303 | 5123401.902 | 47059789.662 | Great River Energy | Great River Energy | Tangentially-fired | Coal |  | Wet Lime FGD | Low NOx Burner Technology w/ Closed-coupled/Separated OFA
ND | Coal Creek | 6030 | 1 | 2016 | 8272.18 |  |  | 89.08% | 9627.6772 | [5 empty] | 4719439.43 | 0.1929 | 0.33641 | 4326.515 | 7642.843 | 4946752.379 | 45437239.425 | Great River Energy | Great River Energy | Tangentially-fired | Coal |  | Wet Lime FGD | Low NOx Burner Technology w/ Closed-coupled/Separated OFA
ND | Coal Creek | 6030 | 1 | 2017 | 6721.15 | SO2 controls added - use 2018 |  | 72.55% | 9711.6308 | 90% | #2 2017 | 2018 |  |  | 3843539.16 | 0.1824 | 0.16587 | 3361.134 | 3095.703 | 4063790.805 | 37327033.425 | Great River Energy | Great River Energy | Tangentially-fired | Coal |  | Wet Lime FGD | Low NOx Burner Technology w/ Closed-coupled/Separated OFA
[6 empty] | Nox @ 0.13 per new controls |  | Average HR = | 9746.7992 | 4768243.2 | 0.13 | 0.143 | 3020.8821 | 3322.9703
ND | Coal Creek | 6030 | 2 | 2014 | 8317.01 |  | 604.8 | 92.11% | 9535.115 | [5 empty] | 4879863.82 | 0.1427 | 0.34127 | 3286.71 | 7939.625 | 5065733.377 | 46530062.947 | Great River Energy | Great River Energy | Tangentially-fired | Coal |  | Wet Lime FGD | Low NOx Burner Technology w/ Closed-coupled/Separated OFA<br>Overfire Air
ND | Coal Creek | 6030 | 2 | 2015 | 8428.92 |  |  | 90.14% | 9643.8494 | [5 empty] | 4775408.14 | 0.1565 | 0.33768 | 3498.768 | 7775.532 | 5013823.023 | 46053317.021 | Great River Energy | Great River Energy | Tangentially-fired | Coal |  | Wet Lime FGD | Low NOx Burner Technology w/ Closed-coupled/Separated OFA<br>Overfire Air
ND | Coal Creek | 6030 | 2 | 2016 | 7194.48 |  |  | 76.56% | 9490.9246 | [5 empty] | 4056301.26 | 0.1359 | 0.29264 | 2563.559 | 5633.1 | 4191280.992 | 38498049.35 | Great River Energy | Great River Energy | Tangentially-fired | Coal |  | Wet Lime FGD | Low NOx Burner Technology w/ Closed-coupled/Separated OFA<br>Overfire Air
ND | Coal Creek | 6030 | 2 | 2017 | 8282.99 | SO2 controls added - use 2018 |  | 89.11% | 9494.9838 | 90% | 2017 | 2018 |  |  | 4721086.13 | 0.13 | 0.14705 | 2889.499 | 3295.882 | 4880275.66 | 44826636.106 | Great River Energy | Great River Energy | Tangentially-fired | Coal |  | Wet Lime FGD | Low NOx Burner Technology w/ Closed-coupled/Separated OFA<br>Overfire Air
[8 empty] | Average HR = | 9541.2182 | 4768243.2 | 0.13 | 0.142 | 2957.1652 | 3230.1343
ND | Coyote | 8222 | B1 | 2014 | 7641.3 |  | 450 | 73.94% | 11046.2723 | [5 empty] | 2914829.11 | 0.6998 | 0.79366 | 11374.474 | 12777.11 | 3505390.931 | 32197995.938 | Montana Dakota Utilities Company, Northern Municipal Power Agency, Northwestern Public Service Company, Otter Tail Power Company | Otter Tail Power Company | Cyclone boiler | Coal | Diesel Oil | Dry Lime FGD
ND | Coyote | 8222 | B1 | 2015 | 8307.78 | derate for mechanical |  | 52.23% | 11052.5737 | [5 empty] | 2058996.7 | 0.7737 | 0.77215 | 8819.867 | 8786.031 | 2477575.788 | 22757212.727 | Montana Dakota Utilities Company, Northern Municipal Power Agency, Northwestern Public Service Company, Otter Tail Power Company | Otter Tail Power Company | Cyclone boiler | Coal | Diesel Oil | Dry Lime FGD
ND | Coyote | 8222 | B1 | 2016 | 6746.34 | separated overfire air added |  | 65.62% | 10477.4429 | [5 empty] | 2586763.02 | 0.5799 | 0.87614 | 7771.838 | 11872.863 | 2950668.065 | 27102661.739 | Montana Dakota Utilities Company, Northern Municipal Power Agency, Northwestern Public Service Company, Otter Tail Power Company | Otter Tail Power Company | Cyclone boiler | Coal | Diesel Oil | Dry Lime FGD | Overfire Air (Began Jun 15, 2016)
ND | Coyote | 8222 | B1 | 2017 | 7594.86 |  |  | 70.48% | 10743.8742 | 85% | 2017 | 2017 |  |  | 2778245.21 | 0.4237 | 0.90079 | 6377.688 | 13443.944 | 3249673.233 | 29849117.098 | Montana Dakota Utilities Company, Northern Municipal Power Agency, Northwestern Public Service Company, Otter Tail Power Company | Otter Tail Power Company | Cyclone boiler | Coal | Diesel Oil | Dry Lime FGD | Overfire Air
[8 empty] | Average HR = | 10830.0408 | 3350700 | 0.4237 | 0.90079 | 7687.6589 | 16344.0936
ND | Leland Olds | 2817 | 1 | 2014 | 6543.49 |  | 216 | 59.19% | 10656.0618 | [5 empty] | 1119902.16 | 0.2344 | 0.069076 | 1373.365 | 412.168 | 1299227.789 | 11933746.601 | Basin Electric Power Cooperative | Basin Electric Power Cooperative | Dry bottom wall-fired boiler | Coal |  | Wet Lime FGD | Low NOx Burner Technology (Dry Bottom only)<br>Overfire Air
ND | Leland Olds | 2817 | 1 | 2015 | 8527.78 |  |  | 80.3% | 10390.2541 | [5 empty] | 1519407.51 | 0.2367 | 0.086302 | 1814.489 | 681.23 | 1718734.007 | 15787030.12 | Basin Electric Power Cooperative | Basin Electric Power Cooperative | Dry bottom wall-fired boiler | Coal |  | Wet Lime FGD | Low NOx Burner Technology (Dry Bottom only)<br>Overfire Air
ND | Leland Olds | 2817 | 1 | 2016 | 8365.72 |  |  | 79.13% | 10397.2626 | [5 empty] | 1497216.68 | 0.2472 | 0.091368 | 1856.03 | 711.164 | 1694775.222 | 15566954.935 | Basin Electric Power Cooperative | Basin Electric Power Cooperative | Dry bottom wall-fired boiler | Coal |  | Wet Lime FGD | Low NOx Burner Technology (Dry Bottom only)<br>Overfire Air
ND | Leland Olds | 2817 | 1 | 2017 | 6747.29 | SNCR Optimized - use 2018 |  | 63.71% | 10381.4784 | 85% | 2018 | 2017 |  |  | 1205582.1 | 0.1768 | 0.088547 | 1120.955 | 554.118 | 1362585.291 | 12515724.527 | Basin Electric Power Cooperative | Basin Electric Power Cooperative | Dry bottom wall-fired boiler | Coal |  | Wet Lime FGD | Low NOx Burner Technology (Dry Bottom only)<br>Overfire Air
[8 empty] | Average HR = | 10456.2642 | 1608336 | 0.147 | 0.088547 | 1236.0632 | 744.5598
ND | Leland Olds | 2817 | 2 | 2014 | 7972.18 |  | 440 | 71.71% | 10257.8215 | [5 empty] | 2763952.59 | 0.3654 | 0.072311 | 5202.498 | 1025.08 | 3086694.104 | 28352132.358 | Basin Electric Power Cooperative | Basin Electric Power Cooperative | Cyclone boiler | Coal |  | Wet Lime FGD | Overfire Air
ND | Leland Olds | 2817 | 2 | 2015 | 6934.67 |  |  | 64.55% | 9940.4178 | [5 empty] | 2487888.14 | 0.3674 | 0.08619 | 4557.372 | 1065.768 | 2692426.264 | 24730647.652 | Basin Electric Power Cooperative | Basin Electric Power Cooperative | Cyclone boiler | Coal |  | Wet Lime FGD | Overfire Air
ND | Leland Olds | 2817 | 2 | 2016 | 8171.92 | SNCR Optimized |  | 76.94% | 10232.2433 | [5 empty] | 2965565.22 | 0.3663 | 0.080209 | 5433.831 | 1216.939 | 3303589.203 | 30344384.881 | Basin Electric Power Cooperative | Basin Electric Power Cooperative | Cyclone boiler | Coal |  | Wet Lime FGD | Overfire Air
ND | Leland Olds | 2817 | 2 | 2017 | 8109.86 |  |  | 76.63% | 10127.7134 | 85% | 2017 | 2017 |  |  | 2953692.89 | 0.2934 | 0.091211 | 4418.016 | 1364.254 | 3256756.428 | 29914154.971 | Basin Electric Power Cooperative | Basin Electric Power Cooperative | Cyclone boiler | Coal |  | Wet Lime FGD | Overfire Air
[8 empty] | Average HR = | 10139.549 | 3276240 | 0.2934 | 0.091211 | 4873.3147 | 1515.0007
ND | Milton R Young | 2823 | B1 | 2014 | 7988.26 |  | 257 | 88.96% | 9551.8147 | [5 empty] | 2002731.74 | 0.3336 | 0.037698 | 3204.584 | 360.574 | 2082651.083 | 19129722.496 | Minnkota Power Cooperative, Inc. | Minnkota Power Cooperative, Inc. | Cyclone boiler | Coal |  | Wet Lime FGD<br>Wet Limestone | Overfire Air<br>Selective Non-catalytic Reduction
ND | Milton R Young | 2823 | B1 | 2015 | 7062.67 |  |  | 77.61% | 10099.3678 | [5 empty] | 1747255.46 | 0.3326 | 0.068686 | 2949.52 | 606.02 | 1921156.568 | 17646175.456 | Minnkota Power Cooperative, Inc. | Minnkota Power Cooperative, Inc. | Cyclone boiler | Coal |  | Wet Lime FGD<br>Wet Limestone | Overfire Air<br>Selective Non-catalytic Reduction
ND | Milton R Young | 2823 | B1 | 2016 | 8433.21 |  |  | 93.53% | 10969.1564 | [5 empty] | 2105675.64 | 0.3312 | 0.078732 | 3840.856 | 909.257 | 2514616.311 | 23097485.5 | Minnkota Power Cooperative, Inc. | Minnkota Power Cooperative, Inc. | Cyclone boiler | Coal |  | Wet Lime FGD<br>Wet Limestone | Overfire Air<br>Selective Non-catalytic Reduction
ND | Milton R Young | 2823 | B1 | 2017 | 8297.83 |  |  | 91.43% | 10507.8549 | 91% | 2017 | 2017 |  |  | 2058278.4 | 0.3301 | 0.08368 | 3578.953 | 904.914 | 2354649.591 | 21628090.813 | Minnkota Power Cooperative, Inc. | Minnkota Power Cooperative, Inc. | Cyclone boiler | Coal |  | Wet Lime FGD<br>Wet Limestone | Overfire Air<br>Selective Non-catalytic Reduction
[8 empty] | Average HR = | 10282.0485 | 2048701.2 | 0.3301 | 0.08368 | 3476.7527 | 881.3479
ND | Milton R Young | 2823 | B2 | 2014 | 6730.27 |  | 477 | 72.23% | 9886.5222 | [5 empty] | 3018255.59 | 0.3348 | 0.11458 | 5003.736 | 1709.589 | 3248683.993 | 29840050.901 | Minnesota Power and Light Company, Minnkota Power Cooperative, Inc., Square Butte Electric Cooperative | Minnkota Power Cooperative, Inc. | Cyclone boiler | Coal |  | Dual Alkali<br>Wet Lime FGD | Overfire Air<br>Selective Non-catalytic Reduction
ND | Milton R Young | 2823 | B2 | 2015 | 8187.38 |  |  | 87.62% | 9938.7933 | [5 empty] | 3661384.54 | 0.3359 | 0.11702 | 6123.337 | 2129.092 | 3961750.539 | 36389744.058 | Square Butte Electric Cooperative | Minnkota Power Cooperative, Inc. | Cyclone boiler | Coal |  | Dual Alkali<br>Wet Lime FGD | Overfire Air<br>Selective Non-catalytic Reduction
ND | Milton R Young | 2823 | B2 | 2016 | 6112.61 |  |  | 64.85% | 9824.0154 | [5 empty] | 2709569.73 | 0.3348 | 0.12991 | 4466.412 | 1728.997 | 2897990.204 | 26618854.87 | Square Butte Electric Cooperative | Minnkota Power Cooperative, Inc. | Cyclone boiler | Coal |  | Dual Alkali<br>Wet Lime FGD | Overfire Air<br>Selective Non-catalytic Reduction
ND | Milton R Young | 2823 | B2 | 2017 | 8487.2 |  |  | 91.23% | 10088.4174 | 91% | 2017 | 2017 |  |  | 3811875.52 | 0.3332 | 0.13041 | 6389.76 | 2507.451 | 4186681.567 | 38455791.347 | Square Butte Electric Cooperative | Minnkota Power Cooperative, Inc. | Cyclone boiler | Coal |  | Dual Alkali<br>Wet Lime FGD | Overfire Air<br>Selective Non-catalytic Reduction
[8 empty] | Average HR = | 9934.4371 | 3802453.2 | 0.3332 | 0.13041 | 6293.3537 | 2463.0762
ND | R M Heskett | 2790 | B2 | 2014 | 8012.32 |  | 75 | 75.04% | 11173.4481 | [5 empty] | 493009.78 | 0.3596 | 0.84904 | 995.124 | 2338.514 | 599717.58 | 5508619.204 | Montana Dakota Utilities Company | Montana Dakota Utilities Company | Bubbling fluidized bed boiler | Coal
ND | R M Heskett | 2790 | B2 | 2015 | 7947.47 |  |  | 70.54% | 11446.0378 | [5 empty] | 463437.24 | 0.3665 | 0.77134 | 988.737 | 2045.804 | 577507.031 | 5304520.146 | Montana Dakota Utilities Company | Montana Dakota Utilities Company | Bubbling fluidized bed boiler | Coal
ND | R M Heskett | 2790 | B2 | 2016 | 7753.7 |  |  | 68.99% | 11543.172 | [5 empty] | 453257.15 | 0.3873 | 0.72129 | 1015.559 | 1886.906 | 569609.875 | 5232025.253 | Montana Dakota Utilities Company | Montana Dakota Utilities Company | Bubbling fluidized bed boiler | Coal
ND | R M Heskett | 2790 | B2 | 2017 | 7887.94 | New SO2 controls in 2017 |  | 69.34% | 11493.5285 | 85% | 2017 | 2018 |  |  | 455535.46 | 0.3706 | 0.56737 | 985.253 | 1485.297 | 570010.664 | 5235709.79 | Montana Dakota Utilities Company | Montana Dakota Utilities Company | Bubbling fluidized bed boiler | Coal |  | Fluidized Bed Limestone Injection (Began Apr 16, 2017)
[8 empty] | Average HR = | 11414.0466 | 558450 | 0.3706 | 0.464 | 1181.1345 | 1478.8084
ND | Spiritwood Station | 56786 | 1 | 2014 | 2769.04 |  | 106.2 | 9.833% | 24637.208 | [5 empty] | 91481.2 | 0.6821 |  | 1293.99 | 1415.325 | 245388.61 | 2253841.356 | Great River Energy | Great River Energy | Circulating fluidized bed boiler | Coal |  | Dry Lime FGD<br>Fluidized Bed Limestone Injection | Overfire Air<br>Selective Non-catalytic Reduction
ND | Spiritwood Station | 56786 | 1 | 2015 | 7213.56 |  |  |  | 37448.5393 | [5 empty] | 133881.03 | 0.0975 |  | 234.962 | 66.847 | 545512.829 | 5013649.018 | Great River Energy | Great River Energy | Circulating fluidized bed boiler | Coal | Pipeline Natural Gas | Dry Lime FGD<br>Fluidized Bed Limestone Injection | Overfire Air<br>Selective Non-catalytic Reduction
ND | Spiritwood Station | 56786 | 1 | 2016 | 8534.68 |  |  |  | #DIV/0! | [6 empty] | 0.0954 |  | 288.612 | 17.24 | 576798.391 | 6177452.003 | Great River Energy | Great River Energy | Circulating fluidized bed boiler | Coal | Pipeline Natural Gas | Dry Lime FGD<br>Fluidized Bed Limestone Injection | Overfire Air<br>Selective Non-catalytic Reduction
ND | Spiritwood Station | 56786 | 1 | 2017 | 8137.81 |  |  |  | #DIV/0! | [6 empty] | 0.1025 |  | 284.422 | 20.502 | 549640.014 | 5627717.603 | Great River Energy | Great River Energy | Circulating fluidized bed boiler | Coal | Liquified Petroleum Gas, Pipeline Natural Gas | Dry Lime FGD<br>Fluidized Bed Limestone Injection | Overfire Air<br>Selective Non-catalytic Reduction
State | Facility Name |  | Unit ID | Year | # of Months Reported |  | SO2 (tons) | Avg. NOx Rate (lb/MMBtu) | NOx (tons) | CO2 (short tons) | Heat Input (MMBtu)
ND | Spiritwood Station |  | 1 | 2018 | 12 |  | 41 | 0.102 | 261.698 | 538577 | 5221238.211
ND | Stanton | 2824 | 1 | 2014 | 8276.07 | [10 empty] | 0.224 |  | 1055.558 | 2493.258 | 1000026.166 | 9534956.173 | Great River Energy | Great River Energy | Dry bottom wall-fired boiler | Coal | Diesel Oil |  | Low NOx Burner Technology (Dry Bottom only)
ND | Stanton | 2824 | 1 | 2015 | 7558.8 | [10 empty] | 0.2072 |  | 872.206 | 2076.295 | 880519.588 | 8395518.63 | Great River Energy | Great River Energy | Dry bottom wall-fired boiler | Coal | Diesel Oil |  | Low NOx Burner Technology (Dry Bottom only)
ND | Stanton | 2824 | 1 | 2016 | 7543.29 | [10 empty] | 0.2191 |  | 1052.295 | 2412.314 | 963783.352 | 9189367.749 | Great River Energy | Great River Energy | Dry bottom wall-fired boiler | Coal | Diesel Oil |  | Low NOx Burner Technology (Dry Bottom only)
ND | Stanton | 2824 | 1 | 2017 | 1247.69 | [10 empty] | 0.2728 |  | 175.341 | 395.065 | 143160.99 | 1365016.089 | Great River Energy | Great River Energy | Dry bottom wall-fired boiler | Coal | Diesel Oil |  | Low NOx Burner Technology (Dry Bottom only)
ND | Stanton | 2824 | 10 | 2014 | 7537.49 | [10 empty] | 0.3128 |  | 606.392 | 97.595 | 408204.735 | 3892143.859 | Great River Energy | Great River Energy | Tangentially-fired | Coal | Diesel Oil | Dry Lime FGD | Low NOx Burner Technology w/ Separated OFA
ND | Stanton | 2824 | 10 | 2015 | 5982.83 | [10 empty] | 0.3562 |  | 580.355 | 88.018 | 341270.611 | 3253928.117 | Great River Energy | Great River Energy | Tangentially-fired | Coal | Diesel Oil | Dry Lime FGD | Low NOx Burner Technology w/ Separated OFA
ND | Stanton | 2824 | 10 | 2016 | 4193.01 | [10 empty] | 0.4045 |  | 489.498 | 66.679 | 252391.796 | 2406471.872 | Great River Energy | Great River Energy | Tangentially-fired | Coal | Diesel Oil | Dry Lime FGD | Low NOx Burner Technology w/ Separated OFA
ND | Stanton | 2824 | 10 | 2017 | 973.66 | [10 empty] | 0.4448 |  | 125.745 | 27.593 | 59469.141 | 567031.423 | Great River Energy | Great River Energy | Tangentially-fired | Coal | Diesel Oil | Dry Lime FGD | Low NOx Burner Technology w/ Separated OFA